## Slide 1: Understanding Space Weather Impact on the UK Gas Pipeline Network
SWIGS Annual Workshop – Cambridge, September 2019
Gemma S Richardson, Alan W P Thomson
British Geological Survey, Edinburgh, UK

## Slide 2: Pipeline Basics
Gas transmission/distribution pipelines usually buried
  Diameters between 3 inch (0.076 m) and 60 inch (1.52 m)
  Carrying flammable gases at pressures up to 410 kg/cm2.
A galvanic current circulates between metal pipe and medium
  Depends on electrical conductivity of the surrounding soil
  May cross terrains of different conductivity
Anti-corrosion method #1: Non-corrosive coatings
  e.g. asphaltic tape
  Deficiences, incomplete application, defects during burial, aging
Rosemary Oakeshott - Gas pipeline internment CC BY-SA 2.0
Anti-corrosion method #2: Cathodic protection
  To avoid anodic current flow from the pipe to the soil
    the corroding object forms the cathode in galvanic cell, the anode being a base metal which is sacrificed to keep the potential of the metal object negative and at a value below its steady state corrosion potential in the soil burial environment (Osella et al, 1998)
  Good protection for steel at -0.85 V using a CuSO4/Cu half cell as the soil contact reference (Feliu and Andrade, 1991)
  This corresponds fairly well to the equilibrium potential of iron in a dilute Fe2+ solution

## Slide 3: UK Pipeline Modelling
UK has extensive high pressure gas transmission network (run by National Grid Gas plc)
  7,600km of pipelines which transport gas from coastal terminals and storage facilities to exit offtake points (to 8 distribution networks and power stations and large industrial consumers)
Pipelines are coated in a low conductance material and maintained at a slightly negative potential in relation to the Earth to minimise corrosion (‘cathodic protection’)
  Space weather takes the pipe-to-soil (PSP) potential into the corrosion regime for the pipe
  Pipeline PSP not previously been modelled in UK
  Somewhat similar to modelling GIC in a power network but with subtle differences (e.g. continuously earthed)
National Grid (CC BY 4.0)
Notes: Previous research in Scandinavia and N America and some in NZ

## Slide 4: Methodology
Following the method of D. Boteler (GJI, 193(1), 98-109, 2013)
Spilt the pipeline up into sections that are short enough that the electric field can be considered constant in each section
Develop ‘equivalent-pi’ circuit to describe induction in the pipeline
Combine equivalent-pi circuits for each section into a nodal admittance network
  Matrix equation involving admittances and current sources
  Solved for voltages at any node in the pipe
Pipe segment A
Pipe segment B
Pipe segment C
Notes: Nodal admittance matrix

## Slide 5: Benchmark Test Network
Main pipeline (thicker line):
  Pipe diameter = 30 inches (762mm)
  Wall thickness = 15.6mm
Branch lines
  Pipe diameter = 15 inches (381mm)
  Wall thickness = 10mm
Pipeline steel resistivity assumed at 0.18x10-3 Ωm (standard value)
Coating conductance assumed at 5x10-6 Sm-2 (typical modern value)
~300 km

## Slide 6: Calculated electrical properties of the pipe
Series impedance, Ωkm-1,
(r0 and r1 are outer and inner radius of the pipe, rho=resistivity)
Parallel admittance, Skm-1,
(C is pipe coating conductance)
 | Series impedance | Parallel admittance | Characteristic impedance (Z0) | Propagation constant (γ)
Main | 0.004921 | 0.011969 | 0.641174 | 0.007675
Branch | 0.015444 | 0.005985 | 1.606393 | 0.009614

## Slide 7: Sanity Check – PSP in the Test Model
Node | Nodal Voltage for 1V/km Northward Electric field |  | Nodal Voltage for 1 V/km Eastward Electric field | 
 | D. Boteler | Our Model | D. Boteler | Our Model
1 | 29.7153 | 29.715939 | -94.2785 | -94.280670
2 | 2.8349 | 2.835069 | -98.6361 | -98.638225
3 | 2.9536 | 2.953804 | -72.3499 | -72.351619
4 | 6.2398 | 6.239826 | -3.5503 | -3.550413
5 | -23.6659 | -23.666313 | 11.0134 | 11.014549
6 | -23.6570 | -23.657365 | 33.5395 | 33.541490
7 | -3.6118 | -3.611995 | 45.8548 | 45.857434
8 | 36.4017 | 36.401818 | 81.0500 | 81.053222
9 | -20.8547 | -20.855088 | 61.9062 | 61.909042
~300 km

## Slide 8: Constructing a ‘Real’ Network
National Grid open source data includes shape-files that detail the pipeline topology
    Pipe name
    Diameter
    Path of each line
However there is ‘missing’ information
  Pipe wall thickness: assumed to be some small % of diameter (currently 2.5%)
  Pipe resistivity: assume 0.18x10-3 Ωm
  Coating conductance: assume 5x10-6 Sm-2
  Data and assumptions from Boteler (2013)
Coloured by pipe radius (mm)
Notes: Need to make assumptions about the “missing” info – use values from Boteler 2013

## Slide 9
Stars are line ends (i.e. no obvious connection to next node) and triangles are junctions
Gap tolerance (i.e. how close nodes need to be to be considered electrically connected) was 6m for this example
In the network (and matrix inversion)
  175483 nodes
  175291 connections
Coloured by pipe name/ID/section
Constructing a ‘Real’ Network

## Slide 10: Uniform 1 V/km Electric Field: North and East
Max |PSP| = 65.2V
Max |PSP| = 45.0 V

## Slide 11: 13th March 1989 Storm
Max |PSP| = 62.40V
Scotland: 55V at 1989-03-13 21:47:00
UK: 57V at 1989-03-13 21:47:00
1989-03-13 21:47:00

## Slide 12: Single Pipe: E-field and PSP
Min = -55.21 V
Max = 51.25 V
E-field and PSP snapshot during the 13th March 1989 storm @ 21:46UT

## Slide 13: Single Pipe: E-field and PSP
E-field and PSP snapshot during the 13th March 1989 storm @ 21:46UT
Min = -28.47 V
Max = 32.37 V

## Slide 14: ‘Halloween Storm’ of 29-31 October 2003
Maximum PSP (V)
Check: Mean PSP = 0V ?

## Slide 15: Comparison: 29th October 2003 & 13th March 1989
PSP at time of max PSP in network

## Slide 16: Next Steps
Sensitivity analysis of PSP versus pipe characteristics
  Diameter, thickness, coating conductance, electrical connectivity
Industry engagement to refine model and build ‘reasonable worst case scenarios’
  Confirm pipe characteristics and connections
Estimated electric field strength and direction during the 13th March 1989 storm at 21:46UT